## Slide 1
Transformers
Unit 202: Principles of electrical science

## Slide 2
Transformers
Self-Inductance
Induced emf | = | - | L.(I2 – I1) | 
 |  |  | t | 
Where: | L | = | Value of inductance in Henrys (H)
 | t | = | Time in seconds (s)
 | I1 and I2 | = | Values of current

## Slide 3
EXAMPLE 1 - If the current flowing through a coil of inductance of 0.7H increases from 2A to 10A in 40 milli seconds, calculate the average value of an induced emf.
Transformers
E | = | - | L.(I2 – I1) | 
 |  |  | t | 
 | = | - | 0.7 x (10 – 2) | 
 |  |  | 40 x 10-3 | 
 | = | - | 0.7 x 8 | 
 |  |  | 40 x 10-3 | 
 | = | - | 5.6 | 
 |  |  | 40 x 10-3 | 
 | = | - 140 volts

## Slide 4
Transformers
Mutual Inductance

## Slide 5
Transformers
Practical transformer

## Slide 6
Transformers
Transformer equation

## Slide 7
EXAMPLE 2 - A transformer connected to a 230 volt 50Hz supply has a primary winding of 1200 turns. Calculate:
The emf induced in a secondary winding of 300 turns.
The number of turns that would be required in the secondary winding, if it is to produce an emf of 100 volts.
The volts per turn there are on the primary and secondary windings in part (a) above.
Transformers
a) |  | V1 | = | N1 | 
 |  | V2 |  | N2 | 
 |  |  | = | 300 | x 230
 |  |  |  | 1200 | 
 |  | V2 | = | N2 | x V1
 |  |  |  | N1 | 
 | = | 57.5V

## Slide 8
EXAMPLE 2 - A transformer connected to a 230 volt 50Hz supply has a primary winding of 1200 turns. Calculate:
The emf induced in a secondary winding of 300 turns.
The number of turns that would be required in the secondary winding, if it is to produce an emf of 100 volts.
The volts per turn there are on the primary and secondary windings in part (a) above.
Transformers
b) |  | V1 | = | N1 | 
 |  | V2 |  | N2 | 
 |  |  | = | 100 | x 1200
 |  |  |  | 230 | 
 |  | N2 | = | V2 | x N1
 |  |  |  | V1 | 
 | = | 521.7 turns

## Slide 9
EXAMPLE 2 - A transformer connected to a 230 volt 50Hz supply has a primary winding of 1200 turns. Calculate:
The emf induced in a secondary winding of 300 turns.
The number of turns that would be required in the secondary winding, if it is to produce an emf of 100 volts.
The volts per turn there are on the primary and secondary windings in part (a) above.
Transformers
c) | Primary volts/turn | = | V1 | 
 |  |  | N1 | 
 |  | N2 | = | 230 | 
 |  |  |  | 1200 | 
 | = | 0.19 volts
 | Secondary volts/turn | = | V2 | 
 |  |  | N2 | 
 |  | N2 | = | 57.5 | 
 |  |  |  | 300 | 
 | = | 0.19 volts

## Slide 10
EXAMPLE 3 - A transformer connected to a 240 volt 50Hz supply has a primary/secondary turns ratio of 20 : 1. Calculate the emf induced in a secondary winding.
Transformers
 |  | V1 | = | N1 | 
 |  | V2 |  | N2 | 
 |  |  | = | 1 | x 240
 |  |  |  | 20 | 
 |  | V2 | = | N2 | x V1
 |  |  |  | N1 | 
 | = | 12 volts

## Slide 11
Transformers are rated by their output capabilities
The output of a transformer is measured in kVA or MVA.
Therefore if a transformer is rated at 20.7kVA at 230 volts, it is capable of delivering a load current of 90 amps.
This is arrived at by dividing the kVA rating by the rated voltage.
Transformers
Since | kVA | = | Volts x amps
Then |  | Amps | = | kVA | 
 |  |  |  | Volts | 
 | = | 90 amperes
eg |  | I | = | 20700VA | 
 |  |  |  | 230V | 

## Slide 12
EXAMPLE 4 - A 50KVA single phase transformer has a turns ratio of 440/20. The primary winding is connected to a 220 Volt 50Hz supply. Calculate:
The secondary voltage on no load.
The approximate values of primary and secondary currents on Full load.
Transformers
a) |  | V1 | = | N1 | 
 |  | V2 |  | N2 | 
 |  |  | = | 20 | x 220
 |  |  |  | 440 | 
 |  | V2 | = | N2 | x V1
 |  |  |  | N1 | 
 | = | 10 volts

## Slide 13
EXAMPLE 4 - A 50KVA single phase transformer has a turns ratio of 440/20. The primary winding is connected to a 220 Volt 50Hz supply. Calculate:
The secondary voltage on no load.
The approximate values of primary and secondary currents on Full load.
Transformers
b) |  | I1 | = | KVA | 
 |  |  |  | V1 | 
 |  |  | = | 50000 | 
 |  |  |  | 220 | 
 | = | 227 amps
 |  | I2 | = | KVA | 
 |  |  |  | V2 | 
 |  |  | = | 50000 | 
 |  |  |  | 10 | 
 | = | 5 000 amps

## Slide 14
The End
Unit 202: Principles of electrical science